Vector Control of Two PMSGs with a Common DC Link for Grid Connected Wind Energy Conversion

| Seyed Mohammad Reza Moosavi Department of Electrical and Electronics Engineering, Shiraz University of Technology, Shiraz, Iran m.moosavi@sutech.ac.ir | Akbar Rahideh Department of Electrical and Electronics Engineering, Shiraz University of Technology, Shiraz, Iran rahide@sutech.ac.ir | Majid Nayeripour Department of Electrical and Electronics Engineering, Shiraz University of Technology, Shiraz, Iran nayeri@sutech.ac.ir | Masoud Jokar Department of Electrical Engineering, Shiraz University, Shiraz, Iran masoudjookar@gmail.com | Amir Hossein Rajaei Department of Electrical and Electronics Engineering, Shiraz University of Technology, Shiraz, Iran rajaei@sutech.ac.ir | Rasool Hemmati Department of Electrical and Electronics Engineering, Shiraz University of Technology, Shiraz, Iran r.hemmati@sutech.ac.ir |
| --- | --- | --- | --- | --- | --- |

Abstract—Wind energy is a prominent area of application of variable-speed generators operating on the constant grid frequency. This paper describes the operation and control of one of these variable-speed wind generators: the direct driven permanent magnet synchronous generator (PMSG). This generator is connected to the power network by means of a fully controlled frequency converter, which consists of a pulse-width-modulation (PWM) rectifier, an intermediate dc circuit, and a PWM inverter. In this study, simultaneous connection of two PMSGs to a common DC link is considered. The power of the generators is transferred to a capacitor; afterwards, it is delivered to the grid according to the demanded level.

Keywords—Wind energy, conversion system, permanent magnet synchronous generator (PMSG), DC-link, back-to-back converters.

# Introduction

During the last two decades, the penetration of wind energy to power systems has significantly been increased worldwide. Among various types of renewable sources of energy, wind energy has had the most growth rate [1]. Recently, numerous control methods have been applied to ease the issues of the power system interfaces and improve their operation. Wind turbines are generally categorized into two groups based on the types of generators and their application: fixed speed and variable speed. Fixed speed generators are designed based on a simple structure; therefore, their price is comparatively low. However, the produced electrical energy is not optimized. Emergence of power electronic-based converters provides a capability to optimally utilize wind power generators in a wide range of speeds. They are designed for addressing the requirements of the power system interface including control of frequency, voltage, active and reactive power and harmonics [2].

Main components of a typical wind energy system are illustrated in Figure 1, including the rotor of the wind turbine, gearbox, generator, power electronic convertor, and transformer for interfacing the power system [3, 4].

Figure 1.   Components of a wind energy system

Figure 2.    Wind turbine system with two active converters on both the generator and the grid sides

Due to low speed of wind, the gearbox usage for absorbing energy at any wind speed is usually inevitable. With regards to capability of permanent magnet (PM) synchronous generators that can produce electrical energy at any wind speed, it is possible to connect the turbine to the generator directly and eliminate the gearbox. These types of generators are designed based on high number of poles; therefore, they can properly work at low speeds [5].

The main advantages that cause increasing usage of PM Synchronous Machines (PMSGs) can be listed as: simple structure, lower weight and volume, and higher efficiency as a result of low level of losses. Although, high price of permanent magnet materials and magnetic characteristic deterioration after long time usage are still considered the weak points of PMSMs [6, 7]. PMSGs are connected to the AC grid via a power electronic converter shown in Figure 2. Applying this converter provides a capability for the generator to adjust its frequency according to the optimized mechanical frequency of the turbine independent of fixed voltage and frequency of the power system.

Converters can be divided in to two parts, generator side and grid side. In the normal operation, the duty of the AC network side convertor is to control the voltage of the DC link [8, 9]. Meanwhile, the converter on the generator side controls the generator speed [10]. The control process of both converters is performed according to the vector control paradigm. In this paper, the connection of two PMSGs to a common DC link by the vector control method is investigated. The produced electric energy by each generator is transferred to a capacitor, considered as the DC link. After controlling the voltage of the capacitor, the demand of the power system is fulfilled at the unity power factor. In section II, the control method of the generator side converter is investigated. The control method of the DC link, which is carried out by the grid side converter, is provided at section III. Section IV is dedicated to the connection of the two PMSGs to a common DC link.

# Control of the Generator Side Convertor

Dynamic equations of a synchronous generator on the rotor flux linkage reference frame are as follows [11, 12]:

usd=-Rsisd-Lsdisddt+Lsωisq			(1)

usq=-Rsisq-Lsdisqdt-Lsωisd+ωψf		(2)

where Ls and Rs are the leakage inductance and the winding resistance of the generator, respectively; usd and usq are the terminal voltage, isd and isq are the d- and q-components of the stator current, ω and ψf are the speed of the generator and the flow of the permanent magnets, respectively. The electromagnetic torque of the PMSG is defined:

Te=32pψfisq 					(3)

where p is the number of pair poles. According to (3), the electromagnetic toque or produced power can be controlled by isq. Cascade controller loops are applied for the controlling purpose. Controlling the current is performed by an inner controller loop, while the outer loop duty is to control the speed of the generator. In this case, the compensator terms are added for improving the dynamic behavior of the system. D-component of the current is used to adjust the generator torque which can be set to zero. It leads to current per torque reduction and subsequently to decrease the ohmic losses of the generator, and the efficiency enhancement [13]. The transfer function of the stator winding current can be concluded from (1) and (2) as follows:

Fs=IsdsUsd's=IsqsUsq's=1Rs+Lss			(4)

where Usd' and Usq' are the dq-components of the voltage to control their corresponding current components, and the s is the Laplace operator. The general scheme of the generator side controller is illustrated in Figure 3.

Figure 3.   Generator side controller

# Grid Side Control Methodology

The dynamic model of the grid connection presented on a reference frame rotating synchronously with the grid voltage space vector is

Vsd=Vtd-Rid-Ldiddt+Lωiq			(5)

Vsq=Vtq-Riq-Ldiqdt-Lωid			(6)

where L and R are the grid inductance and resistance, respectively, and Vtd and Vtq are the inverter voltage components, and Vsd and Vsq are the grid voltage components, and id and iq are the grid current components. If the reference frame is oriented along the supply voltage, the grid voltage vector is

V=Vsd+j0					(7)

Then active and reactive power can be expressed as

P=32Vsdid					(8)

Q=32Vsdiq					(9)

The active and reactive power control can be achieved by controlling the direct and quadrature current components,  respectively. The control of this converter is quite similar to that of the generator. Two control loops are used to control the active and reactive power, respectively [14] (Figure 4).

An outer DC voltage control loop is used to set the d-axis current reference for the active power control. This assures that all the power coming from the rectifier is instantaneously transferred to the grid by the inverter.

The second channel controls the reactive power by setting a q-axis current reference to a current control loop similar to the previous one. The current controllers will provide a voltage reference for the inverter that is compensated by adding rotational electromotive force (EMF) compensation terms. All controllers are proportional-integral (PI) and are tuned using the symmetrical optimum method.

Figure 4.   Inverter control schemes

# Connection of Two PMSGs to a Common DC Link

A.   Topology

In this section, simultaneous connection process of two generators to a common capacitor, shown in Figure 4, is investigated. Two similar PMSGs are used in this investigation. The parameters of the generators and the AC grid are presented respectively in Tables I and II. Output power of the generators are converted to a DC form and stored in a common capacitor via two distinct rectifiers. The grid side inverter transfers the whole amount of the generated energy to the AC grid. The switching frequency is determined by two factors: the power losses of the system and the rating power of the converter. In high power systems, the higher frequency results in higher power losses and the requirement of a more complicated heat dissipating system. Therefore, the switching frequency should be suitably chosen according to the power level [15].

B.   Simulation Results

In this subsection, the results of the considered system including two similar PMSGs connected to the DC link, Figure 5, are presented. The reference speed of both generators is the same. The instant speed of the generators is following the reference speed accurately. In Figure 6, the reference and generators speed are illustrated. In Figure 7, dq-components of the generators currents are shown. As expected, the q-component of current influences the active power, and verifies the absorbed amount of energy by the wind turbine. The reference voltage for the DC link is set at 1500 V, as shown in Figure 8, along with its instantaneous value. The dq-components of the current in the AC side inverter are shown in Fig. 9. The duty of the voltage-source inverter on the grid side is to deliver the required amount of energy. The q-component current is used to set the reactive power to zero. Therefore, the system is working at the unity power factor. The symmetrical and balanced output current of the inverter in the abc system is shown in Figure 10. The generating power summation of the two PMSGs and the delivered power to the AC Grid are shown in Figure 11.

Figure 5.   Connection of two PMSGs to a common DC link

Table I.   Parameters of Generators

| Values | Parameters |
| --- | --- |
| 8.556 mΩ | Stator resistance |
| 3.59 mH | q-component of inductance |
| 3.59 mH | d-component of inductance |
| 120 | Number of pair poles |
| 48500 kg.m2 | Inertia of the machine |
| 5.4015 V.s | Permanent magnet flow |
| 1.74 rads | Machine speed |
| 2MW | Rating Power |
| 690V16.6 Hz | Voltage/Frequency |

Table II.   Parameters of Grid and Converters

| Value of Parameters | Grid & Convertors Parameters |
| --- | --- |
| 720V | line to line voltage |
| 50 Hz | Frequency of network |
| 80 mF | Capacitor |
| 2850Hz | Switching frequency |
| 350 mH | Line & transformer inductance |

Figure 6.   Instantaneous and reference speed of generators

# Conclusion

In this study, the performance of a set of two direct-driven permanent-magnet synchronous generators used in a variable speed wind-energy system is presented. The speed controller sets the generator torque command, which is achieved through a current control loop. The d-components of the generators currents are adjusted at zero to increase the efficiency and to develop optimal torque per unit current. Both PMSGs are connected to a common DC link, and the produced energy is delivered to the AC network via one inverter.

(a)

(b)

Figure 7.   (a) q-component current of generators and its reference; (b) d-component current of generators and its reference

Figure 8.   DC link voltage

(a)

(b)

Figure 9.   (a) q-component current of inverter and its reference; (b) d-component current of Inverter and its reference

Figure 10.   Three-phase output current

Figure 11.   Summation of generating power and delivered power

##### References

[1] R. Zavadil, N. Miller, A. Ellis, and E. Muljadi, “Making connections: Wind generation challenges and progress,” IEEE Power Energy Mag., vol. 3, no. 6, pp. 26–37, Nov. 2005.

- [2] Peake," The History of High Voltage Direct Current Transmission", 3rd Australasian Engineering Heritage Conference 2009.

- [3] Blaabjerg, Z. Chen, and S. B. Kjaer, “Power electronics as efficient interface in dispersed power generation systems,” IEEE Trans. Power Electron., vol. 19, no. 5, pp. 1184–1194, Sep. 2004.

- [4] Chen and F. Blaabjerg, “Wind turbines—A cost effective power source,” Przeglad Elektrotechniczny, no. 5, pp. 464–469, 2004.

[5]. Y. Chen, P. Pillary, and A. Khan, “PM wind generator topologies,” IEEE Trans. Ind. Appl., vol. 41, no. 6, pp. 1619–1626, Nov./Dec. 2005.

[6] H. Polinder, S.W. H. de Haan,M. R. Dubois, and J. Slootweg, “Basic operation principles and electrical conversion systems of wind turbines,” presented at the Nordic Workshop Power Ind. Electron., Trondheim, Norway, Jun. 14–16, 2004.

[7] G. Michalke, A. D. Hansen, and T. Hartkopf, “Control strategy of a variable speed wind turbine with multipole permanent magnet synchronous generator,” presented at the 2007 Eur. Wind Energy Conf. Exhib., Milan, Italy, May 7–10, 2007.

[8] H.-S. Song and K. Nam, “Dual current control scheme for PWM converter under unbalanced input voltage conditions,” IEEE Trans. Ind. Appl., vol. 46, no. 5, pp. 953–959, Oct. 1999.

[9] J.-I. Jang and D.-C. Lee, “High performance control of three-phase PWM converters under nonideal source voltage,” in Proc. IEEE ICIT, Dec.2006, pp. 2791–2796.

[10] S. Li, T. A. Haskew, R. P. Swatloski, and W. Gathings, “Optimal and direct-current vector control of direct-driven PMSG wind turbines,” IEEE Trans. Power. Electron., vol. 27, no. 5, pp. 2325–2337, May 2012.

[11] S. Bernal-Perez, S. Añó-Villalba, R. Blasco-Gimenez, and J. Rodríguez- D’Derlée, “Efficiency and fault ride-through performance of a diode-rectifier- and VSC-inverter-based HVDC link for offshore wind farms,” IEEE Trans. Ind. Electron., vol. 60, no. 6, pp. 2401–2409, Jun. 2013.

[12] J. Kinnunen, J. Pyrhonen, O. Liukkonen, and P. Kurronen, “Analysis of directly network connected non-salient pole permanent magnet synchronous machines,” in Proc. Int. Symp. Ind. Electron., ISIE 2006, Montreal, Canada, Jul. 2006, pp. 2217–2222, 9-3.

[13] W. Leonhard, Control of Electrical Drives. New York: Springer, 1997.

[14] R. Pe˜na, J. C. Clare, and G. M. Asher, “Doubly fed induction generator using back-to-back PWM converters and its application to variable-speed wind-energy generation,” Proc. Inst. Elect. Eng.—Elect. Power Appl., vol. 143, no. 3, pp. 231–241, May 1996.

- [15] A.Yazdani, R.Iravani, “Voltage-Sourced Converters in power systems”, IEEE Press, 2010.